## Slide 1
JD Pool Pumped Storage Project
Engineering Layout and Opinion of Probable Cost
January 6, 2017

## Slide 2: Work Completed to Date
Review of MWH Conceptual Layout
Evaluation of single upper reservoir configuration
  Two alternatives (7,100 / 11,800 AF)
  Modified waterway profile
Preliminary Sizing and Layout of Power Complex
Preliminary Cost Opinion and Project Schedule
Operating Characteristics and Market Products

## Slide 3
Previous Study – Plan View (11,800 AF)

## Slide 4
Previous Study – Waterway Profile

## Slide 5
Alternative 1 – Plan View (7,100 AF)

## Slide 6
Alternative 2 – Plan View (11,800 AF)

## Slide 7
Alternatives 1 and 2 – Waterway Profile

## Slide 8: Energy and Capacity Summary
 | Alternative 1 | Alternative 2
Gross Pool (AF) | 7,100 | 11,800
Energy Storage (MWh) | 14,745 | 25,506
Unit Capacity and Configuration (MW) | 1,200 (3x400) | 1,200 (3x400)
Storage Duration at Full Load (hours) | 14 | 20

## Slide 9: Opinion of Probable Cost
 | Alternative 1 | Alternative 2
Direct Costs |  | 
Reservoirs and Dams1 | $448,100,000 | $714,000,000
Powerhouse Structure Civil Works | $138,000,000 | $138,000,000
Water Conveyance System | $265,000,000 | $265,000,000
Powerhouse E/M Equipment | $850,000,000 | $850,000,000
Additional Directs2 | $444,915,000 | $484,800,000
Subtotal Direct Construction OPCC | $2,146,015,000 | $2,451,800,000
Owner’s Indirect Costs (20%) | $429,203,000 | $490,360,000
Total Construction Direct and Indirect OPCC | $2,575,218,000 | $2,942,160,000
Estimated OPCC ($/MW; $/MWh) | $2,146,000; $175,000 | $2,452,000; $115,000
Notes:
1 – No spillway is assumed to be required for either alternative.
2 – These additional directs are itemized in HDR’s study report.
Transmission, interconnection, and land costs are not included in this cost opinion.

## Slide 10: Conceptual Development Schedule

## Slide 11: Summary of Operating Characteristics
3 x 400 MW Configuration | 
Pumping Efficiency (%) | 89.7
Generating Efficiencies (%) | 84.2 – 87.6 (1,400 – 2,400 cfs)
Plant Cycle Efficiency (%) | ~78

## Slide 12: Summary of Market Products
 | Generate Mode |  |  | Pump Mode |  | 
 | Min MW | Max MW | Incremental Reserves MW | Min MW | Max MW | Decremental Reserves MW
@ Min Head | 183 | 1,099 | 916 | 354 | 1,552 | 1,198
@ Max Head | 111 | 1,200 | 1,089 | 401 | 1,552 | 1,151
Spinning Reserves: Full range of unit operations in < 3 min (gen), < 4 min (pump)
Non-Spin Reserves: Full range of unit operations in < 6 min (gen), < 8 min (pump)